#### 1. WHAT THIS TOOL IS

A vacuum pump removes air, moisture, and contaminants from an HVAC system before refrigerant is added. It creates a deep vacuum that ensures the system operates at peak efficiency and prevents internal corrosion, freezing, and compressor failure.

If manifold gauges are the stethoscope, the vacuum pump is the life-support machine.

#### 2. WHY IT EXISTS / WHEN IT’S USED

Use a vacuum pump when:

- Installing a new HVAC system

- Replacing compressors, coils, or refrigerant lines

- Opening refrigerant circuits for repairs

- Removing moisture and non-condensables from sealed systems

- Preparing a system for refrigerant charging

No vacuum = no warranty.

Any HVAC install without evacuation is malpractice.

#### 3. WHAT PROS DO DIFFERENTLY

Professionals:

✔ Pull vacuum to 500 microns or lower—not “just vacuum”

✔ Use a micron gauge to measure the actual vacuum—not manifold gauges

✔ Conduct a decay test to prove system integrity

✔ Replace vacuum pump oil regularly (moisture contaminates oil instantly)

✔ Use short, large-diameter hoses for faster evacuation

Amateurs:

❌ “Pull it for 10 minutes” and call it done

❌ Use manifold hoses full of contaminants

❌ Skip decay test—leaks go undetected

❌ Think vacuum is time-based instead of micron-based

TradeScout Standard:

“If you didn’t measure the microns, you didn’t do the vacuum.”

#### 4. WHY THIS TOOL MATTERS

Moisture inside HVAC lines causes:

- Acid formation = system corrosion

- Ice crystals = valve blockage

- Compressor overheating = catastrophic failure

- Reduced system efficiency = higher bills + callbacks

This tool prevents silent death inside sealed systems.

#### 5. SAFETY TRAPS

⚠ Hot pump surfaces burn skin

⚠ Incorrect hose removal causes pressure spikes

⚠ Vapors in contaminated oil are hazardous

⚠ Never run pump without oil — destroys pump internally

An HVAC system is only as safe as the vacuum that prepared it.

#### 6. MAINTENANCE CHECKLIST

- Change oil every job or per manufacturer specs

- Keep intake screened from debris

- Store upright to prevent oil migration

- Inspect hoses for cracks and kinks

- Protect from moisture exposure

- Perform vacuum pump performance test quarterly

Clean oil = clean vacuum. Dirty oil = dirty system.

#### 7. CUSTOMER TRUST SIGNALS

Homeowners recognize pros when they:

📌 Show micron readings during evacuation

📌 Explain moisture prevention in one sentence:

“Water in the lines becomes acid. The vacuum removes it.”

📌 Provide photos of final readings

📌 Offer maintenance schedules for system longevity

The vacuum pump is invisible work that creates visible trust.

Documentation here = referral fuel in the TradeScout model.